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Note:
1. Ring flanges available overbored or counterbored per customer specification.2. Bolt holes shall be drilled 1/8th inch larger in diameter than the nominal diameter of the bolt, except for flanges larger than 84 inch in diameter which shall be drilled 3/16th inch larger than the nominal diameter of the bolt.3. Drilling same as ANSI/ASME B16.1 125 lb and B16.5 150 lb pattern.4. Flanges available overdrilled to accommodate insulators.5. AWWA recommends the use of dished head assemblies as alternate to blind flanges, sizes over 72" nominal.6. AWWA C207-01 Class B and D Hub Flanges are identical to Industry Standard Class 125 Light Weight Flanges.
[bookmark: _GoBack]
image1.GIF
N

AWWA C207 - 01

BLIND
0D
BC

B - Hub Flange
Pressure Rating at Atmospheric Temperature:
4" 12" 175 P.S.L 14” & larger 150 P.S.L
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Nominal | 01514 [ gy oy Diilling Hub Diminsions Thickness | Weight {Lbs)
cive. [Dlameter | SB[ "Noof | Hole [Circle | - ¢ e B | Bima
o Holes |Diameter| BC ®
] 900 457 8 0750 750 | 00 0875 5312 062 ) 1
5 | 0 568 8 | 085 B850 | D2 1250 6312 062 9 3
6 | m 672 8 0875 050 | 02 1250 7562 0688 1 18
8 | 3m 872 6 D875 1175 | DFE2 1250 9688 0688 15 7
10 1600 1088 12 1000 1425 068 1250 12000 0688 19 kg
12 1900 1200 12 1000 1700 0f@ 1260 14375 079 D 5
14 200 1419 12 1125 1875 0760 1250 15750 0719 34 75
16 2350 1619 16 1425 2125 0720 1250 18000  0.892 a 15
18 2500 1819 | 16 1250 | 2275 0760 1250 19675 0850 42 127
0 {E W9 0 1250 20) | U070 1250 22000 1040 49 153
2 (2950 2219 | 20 135 | 2725 | 1000 1750 | 24250 | 1.132 &7 213
24 | 30 2419 | o0 1375 | 2951 | 100N 1760 | 2R1%5 | 120 A7 27
26 3435 2619 24 1375 3175 1000 1760 28E00 1307 79 323
28 3B 2819 28 135 3400 (100 1750 30H0 1398 94 33
30 875 019 28 1375 360) 100 1750 32600 1477 104 475
32 4175 3219 2B 1625 385 1125 1750 34750 1581 131 5%
34 | 4375 3419 | 3 1625 | 4D5) 1135 1750 36750 1661 137 73
3% | 4600 3619 | 32 6% | 4275 1426 1750 | 38760 1751 160 | 732
0 4075 019 | T2 1625 | 4525 1425 1750 | 40760 108 105 | 345
40 5075 4019 B 1625 4725 1125 1750 43000 1933 192 1067





